## Slide 1: Fuses vs Circuit Breakers for Low Voltage Applications

## Slide 2: White Paper Outline
Definitions
Interrupting Ratings
Component and System Protection
  Motor Circuit Protection
  Short Circuit Ratings
  Type 1 vs Type 2 Protection
  Power Electronics Applications
Arc Flash Mitigation
Selective Coordination
Maintenance Requirements

## Slide 3: White Paper Outline - Continued
Resetting or Replacing Overcurrent Protective Devices
Diagnostics
Reliability
Obsolescence
Cost of Ownership
Summary
References

## Slide 4: Interrupting Ratings
Fuse
  200kA or Higher (Class J, R, L, CC, T)
  Full Voltage Rating
Circuit Breaker
  7.5, 10, 14, 18, 20, 22, 25, 30, 35, 42, 50, 65, 85, 100,
  125, 150, or 200kA
  Full or Slash Voltage Rating
  Series Rated

## Slide 5: Component & System Protection
Fuses
  Component Protection Often Possible
  Type 2 Protection of Motor Starters & Contactors
  Components Type Tested to 100kA With Class J & CC
  Higher SCCR For Industrial Control Panels
  Test Limiters Reduce Testing Costs
  I2t Protection for Power Electronics
Circuit Breakers
  Protects Conductors
  No Specific Let-thru Limits for CL Breakers
  Type Testing is Limited

## Slide 6: Arc Flash Mitigation
Circuit Breakers
  HRC 0 or 1 Possible
  Higher Incident Energy at Higher Fault Levels
  Advantage vs Fuses above 1200Amp
Fuses
  HRC 0 Likely Above Threshold Current – up to 800A Fuse
  High Energy Possible – Larger Ratings & Low Fault Current

## Slide 7: Selective Coordination
Fuses
  Follow Mfgs Ratio Tables
  Selective Under Overload and Short Circuit
Circuit Breakers
  Selectivity Difficult With Instantaneous Tripping (below 0.1 sec)
  Zone Selective Interlocking May Give Selectivity Below 0.1 sec

## Slide 8: Maintenance Requirements
Circuit Breakers
  Inspection and Preventive Maintenance
  Electrical Performance and Verification Testing (Field Testing)
    Insulation Resistance Test
    Individual Pole Resistance Test
    Inverse-time Overcurrent Trip Test
    Instantaneous Overcurrent Trip Test
    Rated Current Hold-in Test
Fuses
  Inspection and Preventive Maintenance
  Electrical Performance Testing Not Required

## Slide 9: Resetting or Replacing
Circuit Breakers
  Reset on an Overload - OK
  Inspect and Test B4 Reset on a Short Circuit
Fuses
  Replace All Three
  All Should Have Same Catalog Number

## Slide 10: Diagnostics
Fuse
  Open Fuse Indicators Available
  Dissect Blown Fuse To Determine Current Level
Circuit Breaker
  Visual Indication of Status (open, closed, tripped)
  Diagnostics & Communication With Electronic Trip Units

## Slide 11: Reliability
Circuit Breaker
  Affected By Environmental Factors and Previous Interruptions
  May Operate Faster or Slower than Expected
  Lack of Maintenance Reduces Reliability
  Beware of Refurbished Equipment
Fuse
  Less Affected by Environmental Factors
  Tired Fuse May Open Prematurely
  Will Not Operate Slower With Age
  Replace All Three Fuses For Maximum Reliability

## Slide 12: Obsolescence
Circuit Breaker
  Increase in Fault Current may Over-duty CB
  Equipment SCCR Tied to a Specific CB Cat Number
Fuse
  200kA IR Unlikely to Become Obsolete
  Equipment SCCR Tied to Fuse Class Not Specific Mfg

## Slide 13: Cost of Ownership – Real or Perceived?
Initial Cost
  Lowest for Low IR CBs
  Highest for High IR CBs
Maintenance Cost
  Lower for Fuses
  Higher for CBs
Obsolescence Cost
  More Likely to be High with CBs

## Slide 14
Attribute | Fuse | CB
Interrupting Rating | √ | 
Component & System Protection | √ | 
Arc Flash Mitigation | √ | √
Selective Coordination | √ | 
Maintenance Requirements | √ | 
Resetting or Replacing | √ | √
Diagnostics | √ | √
Reliability | √ | 
Obsolescence | √ | 
Cost of Ownership | √ | √
Summary